## Summary
Attachment A – Costing model
The following worksheets are included in this workbook
The contents of this workbook should be read in conjunction with the report
as at 20th January 2015
Worksheet title |  | Description
Input file | Original linetypes | Original linetypes file as provided by AEMC, October 2014 version
| New linetypes (fixed + variable) | Revised input file, combining results of the 'lines output' and 'transformer output' worksheets
| New linetypes (variable only) | Revised input file, combining results of the 'lines output (2)' and 'transformer output (2)' worksheets
Lines | costing model | Details the Line costing model, cost and rating parameters used to generate the input assumptions file
| output | Line input assumptions for variable cost and fixed cost components
| output (2) | Line input assumptions for variable cost only
| attribute scale factors | Line scale factors, to be applied to the line variable cost in the line costing model
| VIC aemc-lines | Regional (VIC) data file with attribute factors incorporated (EXAMPLE ONLY*)
Transformers | costing model | Details the Transformer costing model, cost and rating parameters used to generate the input assumptions file
| output | Transformer input assumptions for variable cost and fixed cost components
| output (2) | Transformer input assumptions for variable cost only
* The sheet VIC aemc-lines is provided to show the formula for the "Overall Factor". This sheet has not been populated with actual data on the attributes of each line.
Version control
| 12th January 2015 | Version provided by EMCa to AEMC, consistent with report of same date
| 20th January 2015 | Version provided by EMCa to AEMC, consistent with report of same date

## Original linetypes
type | from_voltage | to_voltage | size | lumpiness | cost
L | 132 | 132 | L | 75 | 5600
L | 132 | 132 | M | 160 | 3200
L | 132 | 132 | H | 500 | 1500
L | 110 | 110 | L | 75 | 5600
L | 110 | 110 | M | 160 | 3200
L | 110 | 110 | H | 500 | 1500
L | 220 | 220 | L | 970 | 780
L | 220 | 220 | M | 1450 | 650
L | 220 | 220 | H | 2400 | 480
L | 275 | 275 | L | 950 | 775
L | 275 | 275 | M | 1450 | 650
L | 275 | 275 | H | 2400 | 480
L | 330 | 330 | L | 950 | 775
L | 330 | 330 | M | 1450 | 650
L | 330 | 330 | H | 2400 | 480
L | 500 | 500 | L | 2500 | 590
L | 500 | 500 | M | 4250 | 400
L | 500 | 500 | H | 7000 | 240
T | 110 | 132 | L | 150 | 35000
T | 110 | 132 | M | 150 | 35000
T | 110 | 132 | H | 150 | 35000
T | 110 | 220 | L | 150 | 35000
T | 110 | 220 | M | 150 | 35000
T | 110 | 220 | H | 150 | 35000
T | 110 | 275 | L | 150 | 35000
T | 110 | 275 | M | 150 | 35000
T | 110 | 275 | H | 150 | 35000
T | 132 | 220 | L | 150 | 35000
T | 132 | 220 | M | 150 | 35000
T | 132 | 220 | H | 225 | 37500
T | 132 | 275 | L | 150 | 35000
T | 132 | 275 | M | 150 | 35000
T | 132 | 275 | H | 150 | 35000
T | 132 | 330 | L | 225 | 37500
T | 132 | 330 | M | 400 | 24000
T | 132 | 330 | H | 700 | 18000
T | 132 | 500 | L | 600 | 26000
T | 132 | 500 | M | 750 | 22500
T | 132 | 500 | H | 1000 | 19000
T | 165 | 132 | L | 150 | 35000
T | 165 | 132 | M | 150 | 35000
T | 165 | 132 | H | 150 | 35000
T | 165 | 220 | L | 150 | 35000
T | 165 | 220 | M | 150 | 35000
T | 165 | 220 | H | 150 | 35000
T | 220 | 132 | L | 150 | 35000
T | 220 | 132 | M | 150 | 35000
T | 220 | 132 | H | 150 | 35000
T | 220 | 330 | L | 225 | 37500
T | 220 | 330 | M | 400 | 24000
T | 220 | 330 | H | 700 | 18000
T | 220 | 500 | L | 600 | 26000
T | 220 | 500 | M | 750 | 22500
T | 220 | 500 | H | 1000 | 19000
T | 275 | 110 | L | 150 | 35000
T | 275 | 110 | M | 150 | 35000
T | 275 | 110 | H | 150 | 35000
T | 275 | 132 | L | 150 | 35000
T | 275 | 132 | M | 150 | 35000
T | 275 | 132 | H | 150 | 35000
T | 275 | 330 | L | 600 | 26000
T | 275 | 330 | M | 750 | 22500
T | 275 | 330 | H | 1000 | 19000
T | 275 | 500 | L | 370 | 31000
T | 275 | 500 | M | 370 | 31000
T | 275 | 500 | H | 370 | 31000
T | 330 | 132 | L | 225 | 37500
T | 330 | 132 | M | 400 | 24000
T | 330 | 132 | H | 700 | 18000
T | 330 | 220 | L | 225 | 37500
T | 330 | 220 | M | 400 | 24000
T | 330 | 220 | H | 700 | 18000
T | 330 | 500 | L | 1000 | 19000
T | 330 | 500 | M | 1000 | 19000
T | 330 | 500 | H | 1000 | 19000
T | 500 | 132 | L | 600 | 26000
T | 500 | 132 | M | 750 | 22500
T | 500 | 132 | H | 1000 | 19000
T | 500 | 220 | L | 600 | 26000
T | 500 | 220 | M | 750 | 22500
T | 500 | 220 | H | 1000 | 19000
T | 500 | 330 | L | 1000 | 19000
T | 500 | 330 | M | 1000 | 19000
T | 500 | 330 | H | 1000 | 19000
T | 330 | 275 | L | 600 | 26000
T | 330 | 275 | M | 750 | 22500
T | 330 | 275 | H | 1000 | 19000

## New linetypes (fixed+ variable)
type | from_voltage | to_voltage | size | lumpiness | cost(variable) | cost (fixed)
L | 132 | 132 | L | 150 | 2520 | 5600000
L | 132 | 132 | M | 300 | 1400 | 5600000
L | 132 | 132 | H | 360 | 1283.3333 | 5600000
L | 110 | 110 | L | 125 | 3024 | 5600000
L | 110 | 110 | M | 250 | 1680 | 5600000
L | 110 | 110 | H | 300 | 1540 | 5600000
L | 220 | 220 | L | 300 | 2205 | 9800000
L | 220 | 220 | M | 600 | 1225 | 9800000
L | 220 | 220 | H | 720 | 1122.9167 | 9800000
L | 275 | 275 | L | 500 | 1323 | 11800000
L | 275 | 275 | M | 1000 | 735 | 11800000
L | 275 | 275 | H | 1200 | 673.75 | 11800000
L | 330 | 330 | L | 600 | 1102.5 | 12800000
L | 330 | 330 | M | 1200 | 612.5 | 12800000
L | 330 | 330 | H | 1440 | 561.4583 | 12800000
L | 500 | 500 | L | 1250 | 831.6 | 18800000
L | 500 | 500 | M | 2500 | 462 | 18800000
L | 500 | 500 | H | 3000 | 423.5 | 18800000
T | 110 | 132 | L | 50 | 40000 | 1800000
T | 110 | 132 | M | 100 | 20000 | 1800000
T | 110 | 132 | H | 150 | 20000 | 1800000
T | 110 | 220 | L | 100 | 50000 | 2400000
T | 110 | 220 | M | 150 | 33333.3333 | 2400000
T | 110 | 220 | H | 200 | 25000 | 2400000
T | 110 | 275 | L | 150 | 33333.3333 | 3400000
T | 110 | 275 | M | 250 | 20000 | 3400000
T | 110 | 275 | H | 400 | 15000 | 3400000
T | 132 | 220 | L | 100 | 50000 | 2400000
T | 132 | 220 | M | 150 | 33333.3333 | 2400000
T | 132 | 220 | H | 200 | 25000 | 2400000
T | 132 | 275 | L | 150 | 33333.3333 | 3400000
T | 132 | 275 | M | 250 | 20000 | 3400000
T | 132 | 275 | H | 400 | 15000 | 3400000
T | 132 | 330 | L | 225 | 35555.5556 | 3900000
T | 132 | 330 | M | 400 | 22500 | 3900000
T | 132 | 330 | H | 700 | 17142.8571 | 3900000
T | 132 | 500 | L | 600 | 25000 | 6900000
T | 132 | 500 | M | 750 | 21333.3333 | 6900000
T | 132 | 500 | H | 1000 | 18000 | 6900000
T | 165 | 132 | L | 50 | 40000 | 1800000
T | 165 | 132 | M | 100 | 20000 | 1800000
T | 165 | 132 | H | 150 | 20000 | 1800000
T | 165 | 220 | L | 100 | 50000 | 2400000
T | 165 | 220 | M | 150 | 33333.3333 | 2400000
T | 165 | 220 | H | 200 | 25000 | 2400000
T | 220 | 132 | L | 100 | 50000 | 2400000
T | 220 | 132 | M | 150 | 33333.3333 | 2400000
T | 220 | 132 | H | 200 | 25000 | 2400000
T | 220 | 330 | L | 225 | 35555.5556 | 3900000
T | 220 | 330 | M | 400 | 22500 | 3900000
T | 220 | 330 | H | 700 | 17142.8571 | 3900000
T | 220 | 500 | L | 600 | 25000 | 6900000
T | 220 | 500 | M | 750 | 21333.3333 | 6900000
T | 220 | 500 | H | 1000 | 18000 | 6900000
T | 275 | 110 | L | 150 | 33333.3333 | 3400000
T | 275 | 110 | M | 250 | 20000 | 3400000
T | 275 | 110 | H | 400 | 15000 | 3400000
T | 275 | 132 | L | 150 | 33333.3333 | 3400000
T | 275 | 132 | M | 250 | 20000 | 3400000
T | 275 | 132 | H | 400 | 15000 | 3400000
T | 275 | 330 | L | 225 | 35555.5556 | 3900000
T | 275 | 330 | M | 400 | 22500 | 3900000
T | 275 | 330 | H | 700 | 17142.8571 | 3900000
T | 275 | 500 | L | 600 | 25000 | 6900000
T | 275 | 500 | M | 750 | 21333.3333 | 6900000
T | 275 | 500 | H | 1000 | 18000 | 6900000
T | 330 | 132 | L | 225 | 35555.5556 | 3900000
T | 330 | 132 | M | 400 | 22500 | 3900000
T | 330 | 132 | H | 700 | 17142.8571 | 3900000
T | 330 | 220 | L | 225 | 35555.5556 | 3900000
T | 330 | 220 | M | 400 | 22500 | 3900000
T | 330 | 220 | H | 700 | 17142.8571 | 3900000
T | 330 | 500 | L | 750 | 21333.3333 | 6900000
T | 330 | 500 | M | 1000 | 18000 | 6900000
T | 330 | 500 | H | 1500 | 13333.3333 | 6900000
T | 500 | 132 | L | 600 | 25000 | 6900000
T | 500 | 132 | M | 750 | 21333.3333 | 6900000
T | 500 | 132 | H | 1000 | 18000 | 6900000
T | 500 | 220 | L | 600 | 25000 | 6900000
T | 500 | 220 | M | 750 | 21333.3333 | 6900000
T | 500 | 220 | H | 1000 | 18000 | 6900000
T | 500 | 330 | L | 750 | 21333.3333 | 6900000
T | 500 | 330 | M | 1000 | 18000 | 6900000
T | 500 | 330 | H | 1500 | 13333.3333 | 6900000
T | 330 | 275 | L | 225 | 35555.5556 | 3900000
T | 330 | 275 | M | 400 | 22500 | 3900000
T | 330 | 275 | H | 700 | 17142.8571 | 3900000

## New linetypes (variable only)
type | from_voltage | to_voltage | size | lumpiness | cost
L | 132 | 132 | L | 150 | 2893.3333
L | 132 | 132 | M | 300 | 1586.6667
L | 132 | 132 | H | 360 | 1438.8889
L | 110 | 110 | L | 125 | 3472
L | 110 | 110 | M | 250 | 1904
L | 110 | 110 | H | 300 | 1726.6667
L | 220 | 220 | L | 300 | 2531.6667
L | 220 | 220 | M | 600 | 1388.3333
L | 220 | 220 | H | 720 | 1259.0278
L | 275 | 275 | L | 500 | 1559
L | 275 | 275 | M | 1000 | 853
L | 275 | 275 | H | 1200 | 772.0833
L | 330 | 330 | L | 600 | 1315.8333
L | 330 | 330 | M | 1200 | 719.1667
L | 330 | 330 | H | 1440 | 650.3472
L | 500 | 500 | L | 1250 | 982
L | 500 | 500 | M | 2500 | 537.2
L | 500 | 500 | H | 3000 | 486.1667
T | 110 | 132 | L | 50 | 76000
T | 110 | 132 | M | 100 | 38000
T | 110 | 132 | H | 150 | 32000
T | 110 | 220 | L | 100 | 74000
T | 110 | 220 | M | 150 | 49333.3333
T | 110 | 220 | H | 200 | 37000
T | 110 | 275 | L | 150 | 56000
T | 110 | 275 | M | 250 | 33600
T | 110 | 275 | H | 400 | 23500
T | 132 | 220 | L | 100 | 74000
T | 132 | 220 | M | 150 | 49333.3333
T | 132 | 220 | H | 200 | 37000
T | 132 | 275 | L | 150 | 56000
T | 132 | 275 | M | 250 | 33600
T | 132 | 275 | H | 400 | 23500
T | 132 | 330 | L | 225 | 52888.8889
T | 132 | 330 | M | 400 | 32250
T | 132 | 330 | H | 700 | 22714.2857
T | 132 | 500 | L | 600 | 36500
T | 132 | 500 | M | 750 | 30533.3333
T | 132 | 500 | H | 1000 | 24900
T | 165 | 132 | L | 50 | 76000
T | 165 | 132 | M | 100 | 38000
T | 165 | 132 | H | 150 | 32000
T | 165 | 220 | L | 100 | 74000
T | 165 | 220 | M | 150 | 49333.3333
T | 165 | 220 | H | 200 | 37000
T | 220 | 132 | L | 100 | 74000
T | 220 | 132 | M | 150 | 49333.3333
T | 220 | 132 | H | 200 | 37000
T | 220 | 330 | L | 225 | 52888.8889
T | 220 | 330 | M | 400 | 32250
T | 220 | 330 | H | 700 | 22714.2857
T | 220 | 500 | L | 600 | 36500
T | 220 | 500 | M | 750 | 30533.3333
T | 220 | 500 | H | 1000 | 24900
T | 275 | 110 | L | 150 | 56000
T | 275 | 110 | M | 250 | 33600
T | 275 | 110 | H | 400 | 23500
T | 275 | 132 | L | 150 | 56000
T | 275 | 132 | M | 250 | 33600
T | 275 | 132 | H | 400 | 23500
T | 275 | 330 | L | 225 | 52888.8889
T | 275 | 330 | M | 400 | 32250
T | 275 | 330 | H | 700 | 22714.2857
T | 275 | 500 | L | 600 | 36500
T | 275 | 500 | M | 750 | 30533.3333
T | 275 | 500 | H | 1000 | 24900
T | 330 | 132 | L | 225 | 52888.8889
T | 330 | 132 | M | 400 | 32250
T | 330 | 132 | H | 700 | 22714.2857
T | 330 | 220 | L | 225 | 52888.8889
T | 330 | 220 | M | 400 | 32250
T | 330 | 220 | H | 700 | 22714.2857
T | 330 | 500 | L | 750 | 30533.3333
T | 330 | 500 | M | 1000 | 24900
T | 330 | 500 | H | 1500 | 17933.3333
T | 500 | 132 | L | 600 | 36500
T | 500 | 132 | M | 750 | 30533.3333
T | 500 | 132 | H | 1000 | 24900
T | 500 | 220 | L | 600 | 36500
T | 500 | 220 | M | 750 | 30533.3333
T | 500 | 220 | H | 1000 | 24900
T | 500 | 330 | L | 750 | 30533.3333
T | 500 | 330 | M | 1000 | 24900
T | 500 | 330 | H | 1500 | 17933.3333
T | 330 | 275 | L | 225 | 52888.8889
T | 330 | 275 | M | 400 | 32250
T | 330 | 275 | H | 700 | 22714.2857

## Lines - costing model
| Voltage | Size |  |  |  |  | Lumpiness |  |  |  |  | Variable cost |  |  |  |  | Fixed cost |  |  | Fixed cost (as variable) | Total unit cost
| linetypes data |  |  | region lines data | Proposed Ratings |  |  | Variable component |  |  |  |  | Fixed component
[12 empty] | Variable | Line termination |  |  | Reactive compensation | Fixed |  | Reference length | Fixed cost (as variable) | Unit cost
| Voltage | Size | Lumpiness | Rating bands | Reference rating | Rating multiplier | Rating | Line | Easement |  | Total | Total | (each end) | (no. of ends) | (total) |  | Total |  |  |  | Total
| kV | L, M, H | MW | MW |  |  | MW | $m/km | % | $m/km | $m/km | $/MWkm | $m |  | $m | $m | $ | $/MW | km | $/MWkm | $/MWkm | cf variable only | original cost | cf original
L | 132 | L | 75 | 150 | 300 | 0.5 | 150 | 0.36 | 5% | 0.018 | 0.378 | 2520 | 1.8 | 2 | 3.6 | 2 | 5600000 | 37333.3333 | 100 | 373.3333 | 2893.3333 | 1.1481 | 5600 | 0.51667
L | 132 | M | 160 | 300 |  | 1 | 300 | 0.4 | 5% | 0.02 | 0.42 | 1400 | 1.8 | 2 | 3.6 | 2 | 5600000 | 18666.6667 | 100 | 186.6667 | 1586.6667 | 1.1333 | 3200 | 0.49583
L | 132 | H | 500 | 300+ |  | 1.2 | 360 | 0.44 | 5% | 0.022 | 0.462 | 1283.3333 | 1.8 | 2 | 3.6 | 2 | 5600000 | 15555.5556 | 100 | 155.5556 | 1438.8889 | 1.1212 | 1500 | 0.95926
L | 110 | L | 75 | 100 | 250 | 0.5 | 125 | 0.36 | 5% | 0.018 | 0.378 | 3024 | 1.8 | 2 | 3.6 | 2 | 5600000 | 44800 | 100 | 448 | 3472 | 1.1481 | 5600 | 0.62
L | 110 | M | 160 | 250 |  | 1 | 250 | 0.4 | 5% | 0.02 | 0.42 | 1680 | 1.8 | 2 | 3.6 | 2 | 5600000 | 22400 | 100 | 224 | 1904 | 1.1333 | 3200 | 0.595
L | 110 | H | 500 | 250+ |  | 1.2 | 300 | 0.44 | 5% | 0.022 | 0.462 | 1540 | 1.8 | 2 | 3.6 | 2 | 5600000 | 18666.6667 | 100 | 186.6667 | 1726.6667 | 1.1212 | 1500 | 1.1511
L | 220 | L | 970 | 400 | 600 | 0.5 | 300 | 0.63 | 5% | 0.0315 | 0.6615 | 2205 | 2.4 | 2 | 4.8 | 5 | 9800000 | 32666.6667 | 100 | 326.6667 | 2531.6667 | 1.1481 | 780 | 3.2457
L | 220 | M | 1450 | 600 |  | 1 | 600 | 0.7 | 5% | 0.035 | 0.735 | 1225 | 2.4 | 2 | 4.8 | 5 | 9800000 | 16333.3333 | 100 | 163.3333 | 1388.3333 | 1.1333 | 650 | 2.1359
L | 220 | H | 2400 | 600+ |  | 1.2 | 720 | 0.77 | 5% | 0.0385 | 0.8085 | 1122.9167 | 2.4 | 2 | 4.8 | 5 | 9800000 | 13611.1111 | 100 | 136.1111 | 1259.0278 | 1.1212 | 480 | 2.623
L | 275 | L | 950 | 500 | 1000 | 0.5 | 500 | 0.63 | 5% | 0.0315 | 0.6615 | 1323 | 3.4 | 2 | 6.8 | 5 | 11800000 | 23600 | 100 | 236 | 1559 | 1.1784 | 775 | 2.0116
L | 275 | M | 1450 | 1000 |  | 1 | 1000 | 0.7 | 5% | 0.035 | 0.735 | 735 | 3.4 | 2 | 6.8 | 5 | 11800000 | 11800 | 100 | 118 | 853 | 1.1605 | 650 | 1.3123
L | 275 | H | 2400 | 1000+ |  | 1.2 | 1200 | 0.77 | 5% | 0.0385 | 0.8085 | 673.75 | 3.4 | 2 | 6.8 | 5 | 11800000 | 9833.3333 | 100 | 98.3333 | 772.0833 | 1.1459 | 480 | 1.6085
L | 330 | L | 950 | 800 | 1200 | 0.5 | 600 | 0.63 | 5% | 0.0315 | 0.6615 | 1102.5 | 3.9 | 2 | 7.8 | 5 | 12800000 | 21333.3333 | 100 | 213.3333 | 1315.8333 | 1.1935 | 775 | 1.6978
L | 330 | M | 1450 | 1125 |  | 1 | 1200 | 0.7 | 5% | 0.035 | 0.735 | 612.5 | 3.9 | 2 | 7.8 | 5 | 12800000 | 10666.6667 | 100 | 106.6667 | 719.1667 | 1.1741 | 650 | 1.1064
L | 330 | H | 2400 | 1125+ |  | 1.2 | 1440 | 0.77 | 5% | 0.0385 | 0.8085 | 561.4583 | 3.9 | 2 | 7.8 | 5 | 12800000 | 8888.8889 | 100 | 88.8889 | 650.3472 | 1.1583 | 480 | 1.3549
L | 500 | L | 2500 | 1000 | 2500 | 0.5 | 1250 | 0.99 | 5% | 0.0495 | 1.0395 | 831.6 | 6.9 | 2 | 13.8 | 5 | 18800000 | 15040 | 100 | 150.4 | 982 | 1.1809 | 590 | 1.6644
L | 500 | M | 4250 | 3000 |  | 1 | 2500 | 1.1 | 5% | 0.055 | 1.155 | 462 | 6.9 | 2 | 13.8 | 5 | 18800000 | 7520 | 100 | 75.2 | 537.2 | 1.1628 | 400 | 1.343
L | 500 | H | 7000 | 3000+ |  | 1.2 | 3000 | 1.21 | 5% | 0.0605 | 1.2705 | 423.5 | 6.9 | 2 | 13.8 | 5 | 18800000 | 6266.6667 | 100 | 62.6667 | 486.1667 | 1.148 | 240 | 2.0257

## Lines - output
| Voltage | Size | Lumpiness | Cost
|  |  |  | Variable | Fixed
| kV | L, M, H | MW | $/MWkm | $
L | 132 | L | 150 | 2520 | 5600000
L | 132 | M | 300 | 1400 | 5600000
L | 132 | H | 360 | 1283.3333 | 5600000
L | 110 | L | 125 | 3024 | 5600000
L | 110 | M | 250 | 1680 | 5600000
L | 110 | H | 300 | 1540 | 5600000
L | 220 | L | 300 | 2205 | 9800000
L | 220 | M | 600 | 1225 | 9800000
L | 220 | H | 720 | 1122.9167 | 9800000
L | 275 | L | 500 | 1323 | 11800000
L | 275 | M | 1000 | 735 | 11800000
L | 275 | H | 1200 | 673.75 | 11800000
L | 330 | L | 600 | 1102.5 | 12800000
L | 330 | M | 1200 | 612.5 | 12800000
L | 330 | H | 1440 | 561.4583 | 12800000
L | 500 | L | 1250 | 831.6 | 18800000
L | 500 | M | 2500 | 462 | 18800000
L | 500 | H | 3000 | 423.5 | 18800000

## Lines - output (2)
| Voltage | Size | Lumpiness | Cost
| kV | L, M, H | MW | $/MWkm
L | 132 | L | 150 | 2893.3333
L | 132 | M | 300 | 1586.6667
L | 132 | H | 360 | 1438.8889
L | 110 | L | 125 | 3472
L | 110 | M | 250 | 1904
L | 110 | H | 300 | 1726.6667
L | 220 | L | 300 | 2531.6667
L | 220 | M | 600 | 1388.3333
L | 220 | H | 720 | 1259.0278
L | 275 | L | 500 | 1559
L | 275 | M | 1000 | 853
L | 275 | H | 1200 | 772.0833
L | 330 | L | 600 | 1315.8333
L | 330 | M | 1200 | 719.1667
L | 330 | H | 1440 | 650.3472
L | 500 | L | 1250 | 982
L | 500 | M | 2500 | 537.2
L | 500 | H | 3000 | 486.1667

## Attribute scale factors
Short lines
Attribute | Cost scale factor | Description
L | 1 | Long - line length greater than 20km, cost mulitplier is equal to 1
S | 2 | Short - line length less than or equal to 20km, cost mulitplier is equal to 2
Route directness
Attribute | Cost scale factor | Description
D | 1 | Direct - normal proportion of angle / tension structures, typically 10-20% of all structures
I | 1.2 | Indirect - increased proportion of change in angle, typically greater than 20%
Terrain
Attribute | Cost scale factor | Description
R | 1 | Rural, flat conditions
U | 1.2 | Undulating conditions
H | 1.4 | Hilly conditions or difficult access
Soil conditions
Attribute | Cost scale factor | Description
G | 1 | Average soil condition
A | 1.2 | Poor soil strength and structure
P | 1.4 | Poor soil strength and structure with increased risk of subsidence or heavy rock
Built environment
Attribute | Cost scale factor | Description
R | 1 | Average density, typical of rural / outer urban areas
U | 1.5 | Increased density typical of inner urban / built-up areas
Technology
Attribute | Cost scale factor | Description
O | 1 | Overhead - normal overhead line design and construction
U | 8 | Underground - cable design and construction

## VIC aemc-lines
name | from name | to name | admit | cts rating | st rating | type | size | length | dupe | region | from voltage | to voltage | stype | ckt | Short line | Directness | Terrain | Soil | Environment | Technology | Overall Factor
3XNA220_3RED220 | 3XNA220 | 3RED220 | 32.2373 | 132.5 | 132.5 | L | L | 0.49383 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3XNC330_3WOD330 | 3XNC330 | 3WOD330 | 38.3142 | 428.5 | 428.5 | L | M | 0 | 2 | VIC | 330 | 330 | M | 1 | L | D | R | G | R | O | 1
3XND330_3MUR330 | 3XND330 | 3MUR330 | 22.1239 | 357.5 | 357.5 | L | L | 111.7244 | 2 | VIC | 330 | 330 | M | 1 | L | D | R | G | R | O | 1
3XNE132_3MUR132 | 3XNE132 | 3MUR132 | 11.2867 | 34.5 | 45.5 | L | L | 0.49383 | 2 | VIC | 132 | 132 | M | 1 | L | D | R | G | R | O | 1
3XNF330_3MUR330 | 3XNF330 | 3MUR330 | 34.2231 | 357.5 | 357.5 | L | L | 28.2925 | 2 | VIC | 330 | 330 | M | 1 | L | D | R | G | R | O | 1
3HEY275_3XSG275 | 3HEY275 | 3XSG275 | 20.3666 | 496 | 496 | L | L | 0 | 2 | VIC | 275 | 275 | M | 1 | L | D | R | G | R | O | 1
3ALT220_3BRO220 | 3ALT220 | 3BRO220 | 240.0384 | 775 | 775 | L | H | 7.1 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3ALT220_3KEL220 | 3ALT220 | 3KEL220 | 114.3772 | 775.3 | 775.3 | L | H | 14.8 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3APD220_3APD500 | 3APD220 | 3APD500 | 32.5733 | 0 | 0 | T | L | 1 | 1 | VIC | 220 | 500 | M | 1 | [6 empty] | 1
3APD220_3APD500 | 3APD220 | 3APD500 | 32.5733 | 0 | 0 | T | L | 1 | 1 | VIC | 220 | 500 | M | 1 | [6 empty] | 1
3APD220_3APD500 | 3APD220 | 3APD500 | 32.5733 | 0 | 0 | T | L | 1 | 1 | VIC | 220 | 500 | M | 1 | [6 empty] | 1
3APD500_3HEY500 | 3APD500 | 3HEY500 | 294.1176 | 1385.6 | 1385.6 | L | L | 31.8 | 2 | VIC | 500 | 500 | M | 1 | L | D | R | G | R | O | 1
3BAL220_3BEN220 | 3BAL220 | 3BEN220 | 12.6342 | 239.6 | 239.6 | L | L | 96 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3BAL220_3ELA220 | 3BAL220 | 3ELA220 | 76.9231 | 420.1 | 420.1 | L | M | 33.7349 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3BAL220_3MOO220 | 3BAL220 | 3MOO220 | 25.0627 | 239.6 | 239.6 | L | L | 63.6 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3BAL220_3TER220 | 3BAL220 | 3TER220 | 13.9801 | 325 | 325 | L | L | 114.5 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3BAL220_3WBT220 | 3BAL220 | 3WBT220 | 41.841 | 301 | 301 | L | L | 47.2289 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3BEN220_3FOS220 | 3BEN220 | 3FOS220 | 50.5817 | 325.1 | 325.1 | L | L | 23.91 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3BEN220_3KER220 | 3BEN220 | 3KER220 | 13.2608 | 302.3 | 302.3 | L | L | 121.6 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3BOG220_3MBT220 | 3BOG220 | 3MBT220 | 122.6994 | 774 | 774 | L | H | 11.4789 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3BRO220_3FIS220 | 3BRO220 | 3FIS220 | 200 | 823.1 | 823.1 | L | H | 8.3 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3BRO220_3KEL220 | 3BRO220 | 3KEL220 | 113.0071 | 775.3 | 775.3 | L | H | 15 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3BRO220_3NEW220 | 3BRO220 | 3NEW220 | 344.8276 | 751 | 751 | L | H | 4.9 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3BRU220_3RIC220 | 3BRU220 | 3RIC220 | 273.224 | 450 | 450 | L | M | 8.7 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3BRU220_3THO220 | 3BRU220 | 3THO220 | 167.5042 | 751 | 751 | L | H | 8.4085 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3CRA220_3CRA500 | 3CRA220 | 3CRA500 | 54.8246 | 1000 | 1250 | T | M | 1 | 1 | VIC | 220 | 500 | M | 1 | [6 empty] | 1
3CRA220_3EAS220 | 3CRA220 | 3EAS220 | 87.108 | 775 | 775 | L | H | 19.56 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3CRA220_3NRC220 | 3CRA220 | 3NRC220 | 265.1816 | 0 | 0 | L | L | 5.3113 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3CRA220_3TYA220 | 3CRA220 | 3TYA220 | 77.5374 | 0 | 0 | L | L | 21.97 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3CRA500_3HAZ500 | 3CRA500 | 3HAZ500 | 83.682 | 3276.5 | 3276.5 | L | M | 115.75 | 1 | VIC | 500 | 500 | M | 1 | L | D | R | G | R | O | 1
3CRA500_3ROV500 | 3CRA500 | 3ROV500 | 462.963 | 2771.3 | 2771.3 | L | L | 20.86 | 1 | VIC | 500 | 500 | M | 1 | L | D | R | G | R | O | 1
3DED220_3DED330 | 3DED220 | 3DED330 | 31.7259 | 225 | 225 | T | M | 1 | 3 | VIC | 220 | 330 | M | 1 | [6 empty] | 1
3DED220_3GLN220 | 3DED220 | 3GLN220 | 19.7239 | 422.5 | 422.5 | L | M | 81.6 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3DED220_3MBT220 | 3DED220 | 3MBT220 | 32.7869 | 240 | 240 | L | L | 43.8554 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3DED220_3SHE220 | 3DED220 | 3SHE220 | 7.9554 | 239.6 | 239.6 | L | L | 151.92 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3DED330_3MUR330 | 3DED330 | 3MUR330 | 29.1715 | 994 | 994 | L | M | 113.55 | 2 | VIC | 330 | 330 | M | 1 | L | D | R | G | R | O | 1
3DED330_3SOU330 | 3DED330 | 3SOU330 | 14.8148 | 743 | 743 | L | L | 225.3 | 2 | VIC | 330 | 330 | M | 1 | L | D | R | G | R | O | 1
3DED330_3WOD330 | 3DED330 | 3WOD330 | 81.3008 | 743 | 743 | L | L | 41.2 | 1 | VIC | 330 | 330 | M | 1 | L | D | R | G | R | O | 1
3EAS220_3ROW220 | 3EAS220 | 3ROW220 | 900.9009 | 751 | 751 | L | H | 1.85 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3ELA132_3ELA220 | 3ELA132 | 3ELA220 | 9.9602 | 120 | 120 | T | H | 1 | 2 | VIC | 132 | 220 | M | 1 | [6 empty] | 1
3ELA220_3MOO220 | 3ELA220 | 3MOO220 | 37.1471 | 420.1 | 420.1 | L | M | 33.7349 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3EPS220_3MBT220 | 3EPS220 | 3MBT220 | 8.9127 | 239.6 | 239.6 | L | L | 124.8193 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3EPS220_3THO220 | 3EPS220 | 3THO220 | 25.2525 | 479.3 | 479.3 | L | M | 55.7746 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3FIS220_3NEW220 | 3FIS220 | 3NEW220 | 400 | 775.3 | 775.3 | L | H | 4.2 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3FIS220_3WML220 | 3FIS220 | 3WML220 | 442.4779 | 375.5 | 375.5 | L | L | 2.8 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3FOS220_3SHE220 | 3FOS220 | 3SHE220 | 12.9904 | 325.1 | 325.1 | L | L | 93.03 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3GEE220_3KEL220 | 3GEE220 | 3KEL220 | 18.5322 | 239.6 | 239.6 | L | L | 67.3 | 3 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3GEE220_3MOO220 | 3GEE220 | 3MOO220 | 236.4066 | 771.6 | 771.6 | L | H | 7.1 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3GEE220_3POH220 | 3GEE220 | 3POH220 | 40.1929 | 238 | 238 | L | L | 31 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3GLN220_3SHE220 | 3GLN220 | 3SHE220 | 22.7273 | 422.5 | 422.5 | L | M | 70.6 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3HAZ220_3HAZ500 | 3HAZ220 | 3HAZ500 | 35.1494 | 600 | 600 | T | L | 1 | 4 | VIC | 220 | 500 | M | 1 | [6 empty] | 1
3HAZ220_3HWP220 | 3HAZ220 | 3HWP220 | 505.0505 | 749.3 | 749.3 | L | H | 3.48 | 4 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3HAZ500_3LYB500 | 3HAZ500 | 3LYB500 | 666.6667 | 2869.2 | 2869.2 | L | L | 16.8675 | 3 | VIC | 500 | 500 | M | 1 | L | D | R | G | R | O | 1
3HAZ500_3ROV500 | 3HAZ500 | 3ROV500 | 70.922 | 3276.5 | 3276.5 | L | M | 136.6 | 1 | VIC | 500 | 500 | M | 1 | L | D | R | G | R | O | 1
3HAZ500_3SOU500 | 3HAZ500 | 3SOU500 | 62.6959 | 2698.4 | 2698.4 | L | L | 154.2 | 2 | VIC | 500 | 500 | M | 1 | L | D | R | G | R | O | 1
3HEY275_3HEY500 | 3HEY275 | 3HEY500 | 46.083 | 525 | 525 | T | L | 1 | 1 | VIC | 275 | 500 | M | 1 | [6 empty] | 1
3HEY275_3HEY500 | 3HEY275 | 3HEY500 | 46.083 | 370 | 370 | T | L | 1 | 1 | VIC | 275 | 500 | M | 1 | [6 empty] | 1
3HEY500_3MRT500 | 3HEY500 | 3MRT500 | 98.3865 | 2683 | 2683 | L | L | 131.5663 | 1 | VIC | 500 | 500 | M | 1 | L | D | R | G | R | O | 1
3HEY500_3TYR500 | 3HEY500 | 3TYR500 | 114.4165 | 2683 | 2683 | L | L | 74.2169 | 1 | VIC | 500 | 500 | M | 1 | L | D | R | G | R | O | 1
3HOR220_3RED220 | 3HOR220 | 3RED220 | 5.6689 | 302.3 | 302.3 | L | L | 293.494 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3HOR220_3WBT220 | 3HOR220 | 3WBT220 | 11.2994 | 301 | 301 | L | L | 141.6867 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3HTE220_3HWP220 | 3HTE220 | 3HWP220 | 729.927 | 277.3 | 277.3 | L | L | 1.9296 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3HTE220_3MOW220 | 3HTE220 | 3MOW220 | 2272.7273 | 0 | 0 | L | L | 0.61972 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3HWP220_3JEE220 | 3HWP220 | 3JEE220 | 374.5318 | 749.3 | 749.3 | L | H | 29.0155 | 4 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3HWP220_3ROW220 | 3HWP220 | 3ROW220 | 11.4155 | 271.6 | 271.6 | L | L | 123.3803 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3HWP220_3YPS220 | 3HWP220 | 3YPS220 | 88.4956 | 387.7 | 387.7 | L | L | 14.3 | 3 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3JEE220_3MOW220 | 3JEE220 | 3MOW220 | 473.9336 | 375.5 | 375.5 | L | L | 32.6425 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3KEL220_3KEL500 | 3KEL220 | 3KEL500 | 35.7782 | 750 | 750 | T | L | 1 | 3 | VIC | 220 | 500 | M | 1 | [6 empty] | 1
3KEL220_3THO220 | 3KEL220 | 3THO220 | 153.8462 | 543.2 | 543.2 | L | M | 9.1549 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3KEL220_3WML220 | 3KEL220 | 3WML220 | 143.6782 | 745 | 745 | L | H | 12.01 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3KEL500_3SOU500 | 3KEL500 | 3SOU500 | 336.7003 | 2598 | 2598 | L | L | 28.7 | 1 | VIC | 500 | 500 | M | 1 | L | D | R | G | R | O | 1
3KEL500_3SYD500 | 3KEL500 | 3SYD500 | 819.6721 | 1949 | 1949 | L | L | 11.7 | 1 | VIC | 500 | 500 | M | 1 | L | D | R | G | R | O | 1
3KER220_3WET220 | 3KER220 | 3WET220 | 9.4841 | 205 | 205 | L | L | 181.3472 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3LYB500_3LYP220 | 3LYB500 | 3LYP220 | 26.6028 | 0 | 0 | T | L | 1 | 1 | VIC | 500 | 220 | M | 1 | [6 empty] | 1
3MOO220_3MOO500 | 3MOO220 | 3MOO500 | 55.8971 | 1000 | 1250 | T | M | 1 | 2 | VIC | 220 | 500 | M | 1 | [6 empty] | 1
3MOO220_3TER220 | 3MOO220 | 3TER220 | 9.0171 | 239.6 | 239.6 | L | L | 126.7925 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3MOO500_3MRT500 | 3MOO500 | 3MRT500 | 64.3915 | 2598 | 2598 | L | L | 146.73 | 1 | VIC | 500 | 500 | M | 1 | L | D | R | G | R | O | 1
3MOO500_3SYD500 | 3MOO500 | 3SYD500 | 154.5595 | 2521.6 | 2521.6 | L | L | 62.6 | 2 | VIC | 500 | 500 | M | 1 | L | D | R | G | R | O | 1
3MOO500_3TYR500 | 3MOO500 | 3TYR500 | 47.1698 | 2682.5 | 2682.5 | L | L | 208.6792 | 1 | VIC | 500 | 500 | M | 1 | L | D | R | G | R | O | 1
3MUR132_3MUR330 | 3MUR132 | 3MUR330 | 4.1152 | 40 | 40 | T | L | 1 | 2 | VIC | 132 | 330 | M | 1 | [6 empty] | 1
3NRC220_3SRC220 | 3NRC220 | 3SRC220 | 69.5797 | 0 | 0 | L | L | 20.2423 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3RED220_3WET220 | 3RED220 | 3WET220 | 25.9471 | 205 | 205 | L | L | 71.3208 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3RIC220_3ROW220 | 3RIC220 | 3ROW220 | 67.5676 | 585 | 585 | L | M | 25.21 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3RIN220_3ROW220 | 3RIN220 | 3ROW220 | 128.5678 | 701.4 | 701.4 | L | H | 13.1 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3RIN220_3THO220 | 3RIN220 | 3THO220 | 82.6446 | 662 | 662 | L | H | 17.0423 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3ROV220_3ROV500 | 3ROV220 | 3ROV500 | 54.8246 | 1000 | 1250 | T | M | 1 | 2 | VIC | 220 | 500 | M | 1 | [6 empty] | 1
3ROV220_3ROW220 | 3ROV220 | 3ROW220 | 5000.0001 | 0 | 0 | L | L | 0.28169 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3ROV500_3SOU500 | 3ROV500 | 3SOU500 | 251.2563 | 3276.5 | 3276.5 | L | M | 38.79 | 1 | VIC | 500 | 500 | M | 1 | L | D | R | G | R | O | 1
3ROW220_3SPR220 | 3ROW220 | 3SPR220 | 235.849 | 751 | 751 | L | H | 7.42 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3ROW220_3TEM220 | 3ROW220 | 3TEM220 | 74.0741 | 762.1 | 762.1 | L | H | 22.7 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3ROW220_3THO220 | 3ROW220 | 3THO220 | 39.0625 | 591 | 591 | L | M | 36.0563 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3ROW220_3YPS220 | 3ROW220 | 3YPS220 | 11.976 | 269 | 269 | L | L | 105.9 | 4 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3SOU220_3SOU330 | 3SOU220 | 3SOU330 | 41.3223 | 700 | 700 | T | H | 1 | 2 | VIC | 220 | 330 | M | 1 | [6 empty] | 1
3SOU220_3THO220 | 3SOU220 | 3THO220 | 213.2196 | 590 | 590 | L | M | 6.6056 | 2 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3SOU330_3SOU500 | 3SOU330 | 3SOU500 | 84.3882 | 1000 | 1000 | T | L | 1 | 1 | VIC | 330 | 500 | M | 1 | [6 empty] | 1
3SOU500_3SYD500 | 3SOU500 | 3SYD500 | 224.7191 | 2598 | 2598 | L | L | 42.34 | 2 | VIC | 500 | 500 | M | 1 | L | D | R | G | R | O | 1
3TEM220_3THO220 | 3TEM220 | 3THO220 | 158.7302 | 662 | 662 | L | H | 8.8732 | 1 | VIC | 220 | 220 | M | 1 | L | D | R | G | R | O | 1
3TYR132_3TYR500 | 3TYR132 | 3TYR500 | 36.7647 | 0 | 0 | T | L | 1 | 1 | VIC | 132 | 500 | M | 1 | [6 empty] | 1

## Transformers - Costing model
| Voltage |  | Size |  |  |  |  | Lumpiness |  | Variable cost |  | Fixed cost |  | Fixed cost (as variable) | Total unit cost
|  |  |  | aemc linetypes data |  |  | aemc lines data | Proposed Ratings | Variable component |  | Fixed component
Unit cost
| From | To |  | Rating | Cost |  | Ratings |  |  |  | Transformer circuit | Total | reference | Fixed cost (as variable) | Total
| kV | kV | L, M, H | MW | $/MW | $m/MW | MW | MW | $m | $/MW | $m | $ | MW | $/MW | $/MW | cf variable only | original cost | cf original
T | 110 | 132 | L | 150 | 35000 | 0.035 | - | 50 | 2 | 40000 | 1.8 | 1800000 | 50 | 36000 | 76000 | 1.9 | 35000 | 2.1714
T | 110 | 132 | M | 150 | 35000 | 0.035 | 63 | 100 | 2 | 20000 | 1.8 | 1800000 | 100 | 18000 | 38000 | 1.9 | 35000 | 1.0857
T | 110 | 132 | H | 150 | 35000 | 0.035 | - | 150 | 3 | 20000 | 1.8 | 1800000 | 150 | 12000 | 32000 | 1.6 | 35000 | 0.91429
T | 110 | 220 | L | 150 | 35000 | 0.035 | 138-150 | 100 | 5 | 50000 | 2.4 | 2400000 | 100 | 24000 | 74000 | 1.48 | 35000 | 2.1143
T | 110 | 220 | M | 150 | 35000 | 0.035 | 200 | 150 | 5 | 33333.3333 | 2.4 | 2400000 | 150 | 16000 | 49333.3333 | 1.48 | 35000 | 1.4095
T | 110 | 220 | H | 150 | 35000 | 0.035 | 260 | 200 | 5 | 25000 | 2.4 | 2400000 | 200 | 12000 | 37000 | 1.48 | 35000 | 1.0571
T | 110 | 275 | L | 150 | 35000 | 0.035 | - | 150 | 5 | 33333.3333 | 3.4 | 3400000 | 150 | 22666.6667 | 56000 | 1.68 | 35000 | 1.6
T | 110 | 275 | M | 150 | 35000 | 0.035 | 250-275 | 250 | 5 | 20000 | 3.4 | 3400000 | 250 | 13600 | 33600 | 1.68 | 35000 | 0.96
T | 110 | 275 | H | 150 | 35000 | 0.035 | 305-487 | 400 | 6 | 15000 | 3.4 | 3400000 | 400 | 8500 | 23500 | 1.5667 | 35000 | 0.67143
T | 132 | 220 | L | 150 | 35000 | 0.035 | - | 100 | 5 | 50000 | 2.4 | 2400000 | 100 | 24000 | 74000 | 1.48 | 35000 | 2.1143
T | 132 | 220 | M | 150 | 35000 | 0.035 | - | 150 | 5 | 33333.3333 | 2.4 | 2400000 | 150 | 16000 | 49333.3333 | 1.48 | 35000 | 1.4095
T | 132 | 220 | H | 225 | 37500 | 0.0375 | 120 | 200 | 5 | 25000 | 2.4 | 2400000 | 200 | 12000 | 37000 | 1.48 | 37500 | 0.98667
T | 132 | 275 | L | 150 | 35000 | 0.035 | 0-200 | 150 | 5 | 33333.3333 | 3.4 | 3400000 | 150 | 22666.6667 | 56000 | 1.68 | 35000 | 1.6
T | 132 | 275 | M | 150 | 35000 | 0.035 | 250-325 | 250 | 5 | 20000 | 3.4 | 3400000 | 250 | 13600 | 33600 | 1.68 | 35000 | 0.96
T | 132 | 275 | H | 150 | 35000 | 0.035 | 375-500 | 400 | 6 | 15000 | 3.4 | 3400000 | 400 | 8500 | 23500 | 1.5667 | 35000 | 0.67143
T | 132 | 330 | L | 225 | 37500 | 0.0375 | 150-375 | 225 | 8 | 35555.5556 | 3.9 | 3900000 | 225 | 17333.3333 | 52888.8889 | 1.4875 | 37500 | 1.4104
T | 132 | 330 | M | 400 | 24000 | 0.024 | - | 400 | 9 | 22500 | 3.9 | 3900000 | 400 | 9750 | 32250 | 1.4333 | 24000 | 1.3438
T | 132 | 330 | H | 700 | 18000 | 0.018 | 280-400 | 700 | 12 | 17142.8571 | 3.9 | 3900000 | 700 | 5571.4286 | 22714.2857 | 1.325 | 18000 | 1.2619
T | 132 | 500 | L | 600 | 26000 | 0.026 | 0 | 600 | 15 | 25000 | 6.9 | 6900000 | 600 | 11500 | 36500 | 1.46 | 26000 | 1.4038
T | 132 | 500 | M | 750 | 22500 | 0.0225 | - | 750 | 16 | 21333.3333 | 6.9 | 6900000 | 750 | 9200 | 30533.3333 | 1.4313 | 22500 | 1.357
T | 132 | 500 | H | 1000 | 19000 | 0.019 | - | 1000 | 18 | 18000 | 6.9 | 6900000 | 1000 | 6900 | 24900 | 1.3833 | 19000 | 1.3105
T | 165 | 132 | L | 150 | 35000 | 0.035 |  | 50 | 2 | 40000 | 1.8 | 1800000 | 50 | 36000 | 76000 | 1.9 | 35000 | 2.1714
T | 165 | 132 | M | 150 | 35000 | 0.035 |  | 100 | 2 | 20000 | 1.8 | 1800000 | 100 | 18000 | 38000 | 1.9 | 35000 | 1.0857
T | 165 | 132 | H | 150 | 35000 | 0.035 |  | 150 | 3 | 20000 | 1.8 | 1800000 | 150 | 12000 | 32000 | 1.6 | 35000 | 0.91429
T | 165 | 220 | L | 150 | 35000 | 0.035 |  | 100 | 5 | 50000 | 2.4 | 2400000 | 100 | 24000 | 74000 | 1.48 | 35000 | 2.1143
T | 165 | 220 | M | 150 | 35000 | 0.035 |  | 150 | 5 | 33333.3333 | 2.4 | 2400000 | 150 | 16000 | 49333.3333 | 1.48 | 35000 | 1.4095
T | 165 | 220 | H | 150 | 35000 | 0.035 |  | 200 | 5 | 25000 | 2.4 | 2400000 | 200 | 12000 | 37000 | 1.48 | 35000 | 1.0571
T | 220 | 132 | L | 150 | 35000 | 0.035 |  | 100 | 5 | 50000 | 2.4 | 2400000 | 100 | 24000 | 74000 | 1.48 | 35000 | 2.1143
T | 220 | 132 | M | 150 | 35000 | 0.035 |  | 150 | 5 | 33333.3333 | 2.4 | 2400000 | 150 | 16000 | 49333.3333 | 1.48 | 35000 | 1.4095
T | 220 | 132 | H | 150 | 35000 | 0.035 |  | 200 | 5 | 25000 | 2.4 | 2400000 | 200 | 12000 | 37000 | 1.48 | 35000 | 1.0571
T | 220 | 330 | L | 225 | 37500 | 0.0375 | 200 | 225 | 8 | 35555.5556 | 3.9 | 3900000 | 225 | 17333.3333 | 52888.8889 | 1.4875 | 37500 | 1.4104
T | 220 | 330 | M | 400 | 24000 | 0.024 | 225 | 400 | 9 | 22500 | 3.9 | 3900000 | 400 | 9750 | 32250 | 1.4333 | 24000 | 1.3438
T | 220 | 330 | H | 700 | 18000 | 0.018 | 700 | 700 | 12 | 17142.8571 | 3.9 | 3900000 | 700 | 5571.4286 | 22714.2857 | 1.325 | 18000 | 1.2619
T | 220 | 500 | L | 600 | 26000 | 0.026 | 0-750 | 600 | 15 | 25000 | 6.9 | 6900000 | 600 | 11500 | 36500 | 1.46 | 26000 | 1.4038
T | 220 | 500 | M | 750 | 22500 | 0.0225 | 1000 | 750 | 16 | 21333.3333 | 6.9 | 6900000 | 750 | 9200 | 30533.3333 | 1.4313 | 22500 | 1.357
T | 220 | 500 | H | 1000 | 19000 | 0.019 | - | 1000 | 18 | 18000 | 6.9 | 6900000 | 1000 | 6900 | 24900 | 1.3833 | 19000 | 1.3105
T | 275 | 110 | L | 150 | 35000 | 0.035 | - | 150 | 5 | 33333.3333 | 3.4 | 3400000 | 150 | 22666.6667 | 56000 | 1.68 | 35000 | 1.6
T | 275 | 110 | M | 150 | 35000 | 0.035 | 250 | 250 | 5 | 20000 | 3.4 | 3400000 | 250 | 13600 | 33600 | 1.68 | 35000 | 0.96
T | 275 | 110 | H | 150 | 35000 | 0.035 | 459 | 400 | 6 | 15000 | 3.4 | 3400000 | 400 | 8500 | 23500 | 1.5667 | 35000 | 0.67143
T | 275 | 132 | L | 150 | 35000 | 0.035 | - | 150 | 5 | 33333.3333 | 3.4 | 3400000 | 150 | 22666.6667 | 56000 | 1.68 | 35000 | 1.6
T | 275 | 132 | M | 150 | 35000 | 0.035 | - | 250 | 5 | 20000 | 3.4 | 3400000 | 250 | 13600 | 33600 | 1.68 | 35000 | 0.96
T | 275 | 132 | H | 150 | 35000 | 0.035 | 9876 | 400 | 6 | 15000 | 3.4 | 3400000 | 400 | 8500 | 23500 | 1.5667 | 35000 | 0.67143
T | 275 | 330 | L | 600 | 26000 | 0.026 | - | 225 | 8 | 35555.5556 | 3.9 | 3900000 | 225 | 17333.3333 | 52888.8889 | 1.4875 | 26000 | 2.0342
T | 275 | 330 | M | 750 | 22500 | 0.0225 | 1225 | 400 | 9 | 22500 | 3.9 | 3900000 | 400 | 9750 | 32250 | 1.4333 | 22500 | 1.4333
T | 275 | 330 | H | 1000 | 19000 | 0.019 | - | 700 | 12 | 17142.8571 | 3.9 | 3900000 | 700 | 5571.4286 | 22714.2857 | 1.325 | 19000 | 1.1955
T | 275 | 500 | L | 370 | 31000 | 0.031 | 370-525 | 600 | 15 | 25000 | 6.9 | 6900000 | 600 | 11500 | 36500 | 1.46 | 31000 | 1.1774
T | 275 | 500 | M | 370 | 31000 | 0.031 | - | 750 | 16 | 21333.3333 | 6.9 | 6900000 | 750 | 9200 | 30533.3333 | 1.4313 | 31000 | 0.98495
T | 275 | 500 | H | 370 | 31000 | 0.031 | - | 1000 | 18 | 18000 | 6.9 | 6900000 | 1000 | 6900 | 24900 | 1.3833 | 31000 | 0.80323
T | 330 | 132 | L | 225 | 37500 | 0.0375 | - | 225 | 8 | 35555.5556 | 3.9 | 3900000 | 225 | 17333.3333 | 52888.8889 | 1.4875 | 37500 | 1.4104
T | 330 | 132 | M | 400 | 24000 | 0.024 | - | 400 | 9 | 22500 | 3.9 | 3900000 | 400 | 9750 | 32250 | 1.4333 | 24000 | 1.3438
T | 330 | 132 | H | 700 | 18000 | 0.018 | 375 | 700 | 12 | 17142.8571 | 3.9 | 3900000 | 700 | 5571.4286 | 22714.2857 | 1.325 | 18000 | 1.2619
T | 330 | 220 | L | 225 | 37500 | 0.0375 |  | 225 | 8 | 35555.5556 | 3.9 | 3900000 | 225 | 17333.3333 | 52888.8889 | 1.4875 | 37500 | 1.4104
T | 330 | 220 | M | 400 | 24000 | 0.024 |  | 400 | 9 | 22500 | 3.9 | 3900000 | 400 | 9750 | 32250 | 1.4333 | 24000 | 1.3438
T | 330 | 220 | H | 700 | 18000 | 0.018 |  | 700 | 12 | 17142.8571 | 3.9 | 3900000 | 700 | 5571.4286 | 22714.2857 | 1.325 | 18000 | 1.2619
T | 330 | 500 | L | 1000 | 19000 | 0.019 | 1000 | 750 | 16 | 21333.3333 | 6.9 | 6900000 | 750 | 9200 | 30533.3333 | 1.4313 | 19000 | 1.607
T | 330 | 500 | M | 1000 | 19000 | 0.019 | - | 1000 | 18 | 18000 | 6.9 | 6900000 | 1000 | 6900 | 24900 | 1.3833 | 19000 | 1.3105
T | 330 | 500 | H | 1000 | 19000 | 0.019 | - | 1500 | 20 | 13333.3333 | 6.9 | 6900000 | 1500 | 4600 | 17933.3333 | 1.345 | 19000 | 0.94386
T | 500 | 132 | L | 600 | 26000 | 0.026 |  | 600 | 15 | 25000 | 6.9 | 6900000 | 600 | 11500 | 36500 | 1.46 | 26000 | 1.4038
T | 500 | 132 | M | 750 | 22500 | 0.0225 |  | 750 | 16 | 21333.3333 | 6.9 | 6900000 | 750 | 9200 | 30533.3333 | 1.4313 | 22500 | 1.357
T | 500 | 132 | H | 1000 | 19000 | 0.019 |  | 1000 | 18 | 18000 | 6.9 | 6900000 | 1000 | 6900 | 24900 | 1.3833 | 19000 | 1.3105
T | 500 | 220 | L | 600 | 26000 | 0.026 | 0 | 600 | 15 | 25000 | 6.9 | 6900000 | 600 | 11500 | 36500 | 1.46 | 26000 | 1.4038
T | 500 | 220 | M | 750 | 22500 | 0.0225 | - | 750 | 16 | 21333.3333 | 6.9 | 6900000 | 750 | 9200 | 30533.3333 | 1.4313 | 22500 | 1.357
T | 500 | 220 | H | 1000 | 19000 | 0.019 | - | 1000 | 18 | 18000 | 6.9 | 6900000 | 1000 | 6900 | 24900 | 1.3833 | 19000 | 1.3105
T | 500 | 330 | L | 1000 | 19000 | 0.019 |  | 750 | 16 | 21333.3333 | 6.9 | 6900000 | 750 | 9200 | 30533.3333 | 1.4313 | 19000 | 1.607
T | 500 | 330 | M | 1000 | 19000 | 0.019 |  | 1000 | 18 | 18000 | 6.9 | 6900000 | 1000 | 6900 | 24900 | 1.3833 | 19000 | 1.3105
T | 500 | 330 | H | 1000 | 19000 | 0.019 |  | 1500 | 20 | 13333.3333 | 6.9 | 6900000 | 1500 | 4600 | 17933.3333 | 1.345 | 19000 | 0.94386
T | 330 | 275 | L | 600 | 26000 | 0.026 |  | 225 | 8 | 35555.5556 | 3.9 | 3900000 | 225 | 17333.3333 | 52888.8889 | 1.4875 | 26000 | 2.0342
T | 330 | 275 | M | 750 | 22500 | 0.0225 |  | 400 | 9 | 22500 | 3.9 | 3900000 | 400 | 9750 | 32250 | 1.4333 | 22500 | 1.4333
T | 330 | 275 | H | 1000 | 19000 | 0.019 |  | 700 | 12 | 17142.8571 | 3.9 | 3900000 | 700 | 5571.4286 | 22714.2857 | 1.325 | 19000 | 1.1955

## Transformers - output
| Voltage |  | Size | Lumpiness | Cost
| From | To |  |  | Variable | Fixed
| kV | kV | L, M, H | MW | $/MW | $
T | 110 | 132 | L | 50 | 40000 | 1800000
T | 110 | 132 | M | 100 | 20000 | 1800000
T | 110 | 132 | H | 150 | 20000 | 1800000
T | 110 | 220 | L | 100 | 50000 | 2400000
T | 110 | 220 | M | 150 | 33333.3333 | 2400000
T | 110 | 220 | H | 200 | 25000 | 2400000
T | 110 | 275 | L | 150 | 33333.3333 | 3400000
T | 110 | 275 | M | 250 | 20000 | 3400000
T | 110 | 275 | H | 400 | 15000 | 3400000
T | 132 | 220 | L | 100 | 50000 | 2400000
T | 132 | 220 | M | 150 | 33333.3333 | 2400000
T | 132 | 220 | H | 200 | 25000 | 2400000
T | 132 | 275 | L | 150 | 33333.3333 | 3400000
T | 132 | 275 | M | 250 | 20000 | 3400000
T | 132 | 275 | H | 400 | 15000 | 3400000
T | 132 | 330 | L | 225 | 35555.5556 | 3900000
T | 132 | 330 | M | 400 | 22500 | 3900000
T | 132 | 330 | H | 700 | 17142.8571 | 3900000
T | 132 | 500 | L | 600 | 25000 | 6900000
T | 132 | 500 | M | 750 | 21333.3333 | 6900000
T | 132 | 500 | H | 1000 | 18000 | 6900000
T | 165 | 132 | L | 50 | 40000 | 1800000
T | 165 | 132 | M | 100 | 20000 | 1800000
T | 165 | 132 | H | 150 | 20000 | 1800000
T | 165 | 220 | L | 100 | 50000 | 2400000
T | 165 | 220 | M | 150 | 33333.3333 | 2400000
T | 165 | 220 | H | 200 | 25000 | 2400000
T | 220 | 132 | L | 100 | 50000 | 2400000
T | 220 | 132 | M | 150 | 33333.3333 | 2400000
T | 220 | 132 | H | 200 | 25000 | 2400000
T | 220 | 330 | L | 225 | 35555.5556 | 3900000
T | 220 | 330 | M | 400 | 22500 | 3900000
T | 220 | 330 | H | 700 | 17142.8571 | 3900000
T | 220 | 500 | L | 600 | 25000 | 6900000
T | 220 | 500 | M | 750 | 21333.3333 | 6900000
T | 220 | 500 | H | 1000 | 18000 | 6900000
T | 275 | 110 | L | 150 | 33333.3333 | 3400000
T | 275 | 110 | M | 250 | 20000 | 3400000
T | 275 | 110 | H | 400 | 15000 | 3400000
T | 275 | 132 | L | 150 | 33333.3333 | 3400000
T | 275 | 132 | M | 250 | 20000 | 3400000
T | 275 | 132 | H | 400 | 15000 | 3400000
T | 275 | 330 | L | 225 | 35555.5556 | 3900000
T | 275 | 330 | M | 400 | 22500 | 3900000
T | 275 | 330 | H | 700 | 17142.8571 | 3900000
T | 275 | 500 | L | 600 | 25000 | 6900000
T | 275 | 500 | M | 750 | 21333.3333 | 6900000
T | 275 | 500 | H | 1000 | 18000 | 6900000
T | 330 | 132 | L | 225 | 35555.5556 | 3900000
T | 330 | 132 | M | 400 | 22500 | 3900000
T | 330 | 132 | H | 700 | 17142.8571 | 3900000
T | 330 | 220 | L | 225 | 35555.5556 | 3900000
T | 330 | 220 | M | 400 | 22500 | 3900000
T | 330 | 220 | H | 700 | 17142.8571 | 3900000
T | 330 | 500 | L | 750 | 21333.3333 | 6900000
T | 330 | 500 | M | 1000 | 18000 | 6900000
T | 330 | 500 | H | 1500 | 13333.3333 | 6900000
T | 500 | 132 | L | 600 | 25000 | 6900000
T | 500 | 132 | M | 750 | 21333.3333 | 6900000
T | 500 | 132 | H | 1000 | 18000 | 6900000
T | 500 | 220 | L | 600 | 25000 | 6900000
T | 500 | 220 | M | 750 | 21333.3333 | 6900000
T | 500 | 220 | H | 1000 | 18000 | 6900000
T | 500 | 330 | L | 750 | 21333.3333 | 6900000
T | 500 | 330 | M | 1000 | 18000 | 6900000
T | 500 | 330 | H | 1500 | 13333.3333 | 6900000
T | 330 | 275 | L | 225 | 35555.5556 | 3900000
T | 330 | 275 | M | 400 | 22500 | 3900000
T | 330 | 275 | H | 700 | 17142.8571 | 3900000

## Transformers - output (2)
| Voltage |  | Size | Lumpiness | Cost
| From | To
| kV | kV | L, M, H | MW | $/MW
T | 110 | 132 | L | 50 | 76000
T | 110 | 132 | M | 100 | 38000
T | 110 | 132 | H | 150 | 32000
T | 110 | 220 | L | 100 | 74000
T | 110 | 220 | M | 150 | 49333.3333
T | 110 | 220 | H | 200 | 37000
T | 110 | 275 | L | 150 | 56000
T | 110 | 275 | M | 250 | 33600
T | 110 | 275 | H | 400 | 23500
T | 132 | 220 | L | 100 | 74000
T | 132 | 220 | M | 150 | 49333.3333
T | 132 | 220 | H | 200 | 37000
T | 132 | 275 | L | 150 | 56000
T | 132 | 275 | M | 250 | 33600
T | 132 | 275 | H | 400 | 23500
T | 132 | 330 | L | 225 | 52888.8889
T | 132 | 330 | M | 400 | 32250
T | 132 | 330 | H | 700 | 22714.2857
T | 132 | 500 | L | 600 | 36500
T | 132 | 500 | M | 750 | 30533.3333
T | 132 | 500 | H | 1000 | 24900
T | 165 | 132 | L | 50 | 76000
T | 165 | 132 | M | 100 | 38000
T | 165 | 132 | H | 150 | 32000
T | 165 | 220 | L | 100 | 74000
T | 165 | 220 | M | 150 | 49333.3333
T | 165 | 220 | H | 200 | 37000
T | 220 | 132 | L | 100 | 74000
T | 220 | 132 | M | 150 | 49333.3333
T | 220 | 132 | H | 200 | 37000
T | 220 | 330 | L | 225 | 52888.8889
T | 220 | 330 | M | 400 | 32250
T | 220 | 330 | H | 700 | 22714.2857
T | 220 | 500 | L | 600 | 36500
T | 220 | 500 | M | 750 | 30533.3333
T | 220 | 500 | H | 1000 | 24900
T | 275 | 110 | L | 150 | 56000
T | 275 | 110 | M | 250 | 33600
T | 275 | 110 | H | 400 | 23500
T | 275 | 132 | L | 150 | 56000
T | 275 | 132 | M | 250 | 33600
T | 275 | 132 | H | 400 | 23500
T | 275 | 330 | L | 225 | 52888.8889
T | 275 | 330 | M | 400 | 32250
T | 275 | 330 | H | 700 | 22714.2857
T | 275 | 500 | L | 600 | 36500
T | 275 | 500 | M | 750 | 30533.3333
T | 275 | 500 | H | 1000 | 24900
T | 330 | 132 | L | 225 | 52888.8889
T | 330 | 132 | M | 400 | 32250
T | 330 | 132 | H | 700 | 22714.2857
T | 330 | 220 | L | 225 | 52888.8889
T | 330 | 220 | M | 400 | 32250
T | 330 | 220 | H | 700 | 22714.2857
T | 330 | 500 | L | 750 | 30533.3333
T | 330 | 500 | M | 1000 | 24900
T | 330 | 500 | H | 1500 | 17933.3333
T | 500 | 132 | L | 600 | 36500
T | 500 | 132 | M | 750 | 30533.3333
T | 500 | 132 | H | 1000 | 24900
T | 500 | 220 | L | 600 | 36500
T | 500 | 220 | M | 750 | 30533.3333
T | 500 | 220 | H | 1000 | 24900
T | 500 | 330 | L | 750 | 30533.3333
T | 500 | 330 | M | 1000 | 24900
T | 500 | 330 | H | 1500 | 17933.3333
T | 330 | 275 | L | 225 | 52888.8889
T | 330 | 275 | M | 400 | 32250
T | 330 | 275 | H | 700 | 22714.2857